## HMI
[8 empty] | Communications Interfaces s - shared port o - optional w/ comm module | [21 empty] | Memory (MB) |  | Dimensions (mm)
Platform | Cat. No. | Full Description | Basic Description | Type | Size | Color | Options | RS-232 | RS-233 (DF1) | RS-234 (DH-485) | RS-485 | DH-485 | DH+ | RIO | DeviceNet | ControlNet | Ethernet/IP | ProfiNet | Profibus | Modbus RTU | Modbus TCP/IP | Mitsubishi (MC TCP/IP) | Mitsubishi (FX) | OMRON (FINS TCP) | OMRON (LINK/Multilink) | OPC UA Client | OPC UA Server | USB | Input Power | Nonvolatile | RAM | W (Bezel) | H (Bezel) | D (Total) | D (in Cab.) | W (Cutout) | H (Cutout) | Notes | Migration Component | Description | Notes
PanelView | 2711-K3A10L1 | PanelView 300, 3 in, Monochrome, Keypad, DC | PanelView 300 | Keypad | 3 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 140 | 197 | 82 | 69 | 109 | 178 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K3A17L1 | PanelView 300, 3 in, Monochrome, Keypad, DC | PanelView 300 | Keypad | 3 in | Monochrome |  |  | 1 | [19 empty] | DC | 0.24 | 0.17 | 140 | 197 | 82 | 69 | 109 | 178 | This terminal does not have an RS-232 printer port. Use the communication port to download or upload application files. | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-K3A2L1 | PanelView 300, 3 in, Monochrome, Keypad, DC | PanelView 300 | Keypad | 3 in | Monochrome | [5 empty] | 1 | [16 empty] | DC | 0.24 | 0.17 | 140 | 197 | 82 | 69 | 109 | 178 | Terminals with a DH-485 communication port require application uploads and downloads through the communication port. The RS-232 printer port is only for printing only. | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K3A5L1 | PanelView 300, 3 in, Monochrome, Keypad, DC | PanelView 300 | Keypad | 3 in | Monochrome |  |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 140 | 197 | 82 | 69 | 109 | 178 | Terminals with a DH-485 communication port require application uploads and downloads through the communication port. The RS-232 printer port is only for printing only. | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-K3A5L1K | PanelView 300, 3 in, Monochrome, Keypad, DC, Conformal Coated | PanelView 300 | Keypad | 3 in | Monochrome | Conformal Coated | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 140 | 197 | 82 | 69 | 109 | 178 | Terminals with a DH-485 communication port require application uploads and downloads through the communication port. The RS-232 printer port is only for printing only. K at the end of a catalog number means the terminal is conformal-coated. | 6AG1124-1DC01-4AX0 | KP400 Comfort SIPLUS, 4.3 in, Color, Keypad, DC, Conformal Coated | Panel cutout is smaller, filler plate required.
PanelView | 2711-M3A18L1 | PanelView 300 Micro, 3 in, Monochrome, Keypad, DC | PanelView 300 Micro | Keypad | 3 in | Monochrome |  |  | 1 | [19 empty] | DC | 0.24 |  | 133 | 111 | 48 | 35 | 102 | 92 | These terminals do not have an RS-232 printer port. Use the communication port to upload and download application files. | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC
PanelView | 2711-M3A19L1 | PanelView 300 Micro, 3 in, Monochrome, Keypad, DC | PanelView 300 Micro | Keypad | 3 in | Monochrome |  |  |  | 1 | [18 empty] | DC | 0.24 |  | 133 | 111 | 48 | 35 | 102 | 92 | These terminals do not have an RS-232 printer port. Use the communication port to upload and download application files. | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC
PanelView | 2711-B5A1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-B5A10 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B5A10L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B5A12 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [20 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A14 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome | [8 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B5A15 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-B5A15L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-B5A16 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | 1 | [19 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A16L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | 1 | [19 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A1L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-B5A2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome | [5 empty] | 1 | [16 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B5A20 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [8 empty] | 1 | [11 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A20L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | [8 empty] | 1 | [11 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A2L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless |  |  |  |  | 1 | [16 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B5A3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B5A3L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B5A5 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  |  |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A5L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless |  |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A8 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-B5A8L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-B5A9 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A9L2 | PanelView 550, 5.5 in, Monochrome, Key/Touch, AC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A10L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B5A10L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B5A12L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [20 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A14L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome | [8 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B5A15L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-B5A15L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-B5A16L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | 1 | [19 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A16L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | 1 | [19 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A1L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-B5A1L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-B5A20L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A20L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A2L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome | [5 empty] | 1 | [16 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B5A2L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless |  |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B5A3L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B5A3L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B5A5L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A5L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A8L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-B5A8L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-B5A9L1 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC | PanelView 550 | Key/Touch | 5.5 in | Monochrome |  | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B5A9L3 | PanelView 550, 5.5 in, Monochrome, Key/Touch, DC, Stainless | PanelView 550 | Key/Touch | 5.5 in | Monochrome | Stainless | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Stainless faceplate not available, replacement component IP65. Panel cutout is smaller, filler plate required.
PanelView | 2711-K5A1 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K5A10 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K5A10L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K5A12 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [20 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A14 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome | [8 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K5A15 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K5A15L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K5A16 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | 1 | [19 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A16L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | 1 | [19 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A1L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K5A2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome | [5 empty] | 1 | [16 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K5A20 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [8 empty] | 1 | [11 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A20L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | [8 empty] | 1 | [11 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A2L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless |  |  |  |  | 1 | [16 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K5A3 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K5A3L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K5A5 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  |  |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A5L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless |  |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A8 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K5A8L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K5A9 | PanelView 550, 5.5 in, Monochrome, Keypad, AC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A9L2 | PanelView 550, 5.5 in, Monochrome, Keypad, AC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required.
PanelView | 2711-K5A10L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K5A10L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K5A12L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [20 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K5A14L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome | [8 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K5A15L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K5A15L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K5A16L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | 1 | [19 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K5A16L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | 1 | [19 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65.
PanelView | 2711-K5A1L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K5A1L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K5A20L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K5A20L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65.
PanelView | 2711-K5A2L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome | [5 empty] | 1 | [16 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K5A2L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless |  |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K5A3L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K5A3L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K5A5L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K5A5L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65.
PanelView | 2711-K5A8L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K5A8L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K5A9L1 | PanelView 550, 5.5 in, Monochrome, Keypad, DC | PanelView 550 | Keypad | 5.5 in | Monochrome |  | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K5A9L3 | PanelView 550, 5.5 in, Monochrome, Keypad, DC, Stainless | PanelView 550 | Keypad | 5.5 in | Monochrome | Stainless | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 266 | 167 | 106 | 86 | 243 | 144 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65.
PanelView | 2711-T5A10L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T5A12L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 | [20 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-T5A14L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome | [8 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T5A15L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T5A16L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 | 1 | [19 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-T5A1L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T5A20L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-T5A2L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome | [5 empty] | 1 | [16 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T5A3L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T5A5L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-T5A8L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T5A9L1 | PanelView 550, 5.5 in, Monochrome, Touch, DC | PanelView 550 | Touch | 5.5 in | Monochrome |  | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 185 | 152 | 82 | 64 | 165 | 125 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-B6C1 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-B6C10 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B6C12 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [20 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C14 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color | [8 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B6C15 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-B6C16 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | 1 | [19 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C2 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color | [5 empty] | 1 | [16 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B6C20 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C3 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B6C5 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  |  |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C8 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-B6C9 | PanelView 600, 5 in, Color, Key/Touch, AC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C10L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B6C12L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [20 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C14L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color | [8 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-B6C15L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-B6C16L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | 1 | [19 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C1L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-B6C20L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C2L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color | [5 empty] | 1 | [16 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B6C3L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-B6C5L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-B6C8L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-B6C9L1 | PanelView 600, 5 in, Color, Key/Touch, DC | PanelView 600 | Key/Touch | 5 in | Color |  | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView | 2711-K6C1 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K6C10 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K6C12 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [20 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K6C14 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color | [8 empty] | 1 | [13 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K6C15 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K6C16 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 | 1 | [19 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K6C2 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color | [5 empty] | 1 | [16 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K6C20 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K6C3 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K6C5 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  |  |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K6C8 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K6C9 | PanelView 600, 5 in, Color, Keypad, AC | PanelView 600 | Keypad | 5 in | Color |  | 1 |  | 1 | [18 empty] | AC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K6C10L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K6C12L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [20 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K6C14L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color | [8 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K6C15L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K6C16L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 | 1 | [19 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K6C1L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K6C20L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K6C2L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color | [5 empty] | 1 | [16 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K6C3L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K6C5L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-K6C8L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K6C9L1 | PanelView 600, 5 in, Color, Keypad, DC | PanelView 600 | Keypad | 5 in | Color |  | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 290 | 192 | 116 | 91 | 264 | 167 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView | 2711-T6C10L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T6C12L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 | [20 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-T6C14L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color | [8 empty] | 1 | [13 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T6C15L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T6C16L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 | 1 | [19 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-T6C1L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T6C20L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-T6C2L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color | [5 empty] | 1 | [16 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T6C3L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T6C5L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  |  |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-T6C8L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T6C9L1 | PanelView 600, 5 in, Color, Touch, DC | PanelView 600 | Touch | 5 in | Color |  | 1 |  | 1 | [18 empty] | DC | 0.24 | 0.17 | 185 | 152 | 96 | 79 | 165 | 125 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView | 2711-K9C1 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K9C10 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K9C12 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [20 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K9C14 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color | [8 empty] | 1 | [13 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K9C15 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K9C16 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 | 1 | [19 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K9C20 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K9C3 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K9C8 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K9C9 | PanelView 900, 9 in, Color, Keypad, AC | PanelView 900 | Keypad | 9 in | Color |  | 1 |  | 1 | [18 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K9C10L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K9C12L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [20 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K9C14L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color | [8 empty] | 1 | [13 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K9C15L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K9C16L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 | 1 | [19 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K9C1L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K9C20L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K9C3L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K9C8L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K9C9L1 | PanelView 900, 9 in, Color, Keypad, DC | PanelView 900 | Keypad | 9 in | Color |  | 1 |  | 1 | [18 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K9A1 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K9A10 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K9A12 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | [20 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K9A14 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome | [8 empty] | 1 | [13 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K9A15 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K9A16 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | 1 | [19 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K9A2 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome | [5 empty] | 1 | [16 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K9A3 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K9A5 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  |  |  | 1 | [18 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K9A8 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K9A9 | PanelView 900, 9 in, Monochrome, Keypad, AC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 |  | 1 | [18 empty] | AC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K9A10L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K9A12L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | [20 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K9A14L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome | [8 empty] | 1 | [13 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K9A15L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K9A16L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | 1 | [19 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K9A1L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K9A2L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome | [5 empty] | 1 | [16 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K9A3L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K9A5L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  |  |  | 1 | [18 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K9A8L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K9A9L1 | PanelView 900, 9 in, Monochrome, Keypad, DC | PanelView 900 | Keypad | 9 in | Monochrome |  | 1 |  | 1 | [18 empty] | DC | 0.24 |  | 406 | 249 | 112 | 90 | 375 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-T9C1 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T9C10 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T9C12 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 | [20 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T9C14 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color | [8 empty] | 1 | [13 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T9C15 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T9C16 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 | 1 | [19 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T9C20 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T9C3 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T9C8 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T9C9 | PanelView 900, 9 in, Color, Touch, AC | PanelView 900 | Touch | 9 in | Color |  | 1 |  | 1 | [18 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T9C10L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T9C12L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 | [20 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T9C14L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color | [8 empty] | 1 | [13 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T9C15L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T9C16L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 | 1 | [19 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T9C1L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T9C20L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T9C3L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T9C8L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T9C9L1 | PanelView 900, 9 in, Color, Touch, DC | PanelView 900 | Touch | 9 in | Color |  | 1 |  | 1 | [18 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T9A1 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T9A10 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T9A12 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | [20 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T9A14 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome | [8 empty] | 1 | [13 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T9A15 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T9A16 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | 1 | [19 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T9A2 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome | [5 empty] | 1 | [16 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T9A3 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T9A5 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  |  |  | 1 | [18 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T9A8 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T9A9 | PanelView 900, 9 in, Monochrome, Touch, AC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 |  | 1 | [18 empty] | AC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T9A10L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | [6 empty] | 1 | [13 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T9A12L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | [20 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T9A14L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome | [8 empty] | 1 | [13 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T9A15L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | [7 empty] | 1 | [12 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T9A16L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | 1 | [19 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T9A1L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 | [5 empty] | 1 | [14 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T9A2L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome | [5 empty] | 1 | [16 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T9A3L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 |  |  |  | 1 | [16 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T9A5L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  |  |  | 1 | [18 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T9A8L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T9A9L1 | PanelView 900, 9 in, Monochrome, Touch, DC | PanelView 900 | Touch | 9 in | Monochrome |  | 1 |  | 1 | [18 empty] | DC | 0.24 |  | 336 | 249 | 112 | 90 | 305 | 224 | 1008K memory for PV900M (Series E, firmware 3.0 or later) and PV900C | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-K10C1 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K10C10 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K10C12 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [20 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K10C14 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color | [8 empty] | 1 | [13 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K10C15 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K10C16 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | 1 | [19 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K10C20 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K10C3 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 |  |  |  | 1 | [16 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K10C8 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K10C9 | PanelView 1000, 10 in, Color, Keypad, AC | PanelView 1000 | Keypad | 10 in | Color |  | 1 |  | 1 | [18 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K10C10L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K10C12L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [20 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K10C14L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color | [8 empty] | 1 | [13 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K10C15L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K10C16L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | 1 | [19 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K10C1L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K10C20L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K10C3L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 |  |  |  | 1 | [16 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K10C8L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K10C9L1 | PanelView 1000, 10 in, Color, Keypad, DC | PanelView 1000 | Keypad | 10 in | Color |  | 1 |  | 1 | [18 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K10G1 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [5 empty] | 1 | [14 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K10G10 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [6 empty] | 1 | [13 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K10G12 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [20 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K10G14 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale | [8 empty] | 1 | [13 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K10G15 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [7 empty] | 1 | [12 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K10G16 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | 1 | [19 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K10G20 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [8 empty] | 1 | [11 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K10G3 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 |  |  |  | 1 | [16 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K10G8 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K10G9 | PanelView 1000, 10 in, Grayscale, Keypad, AC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 |  | 1 | [18 empty] | AC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-K10G10L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [6 empty] | 1 | [13 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K10G12L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [20 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K10G14L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale | [8 empty] | 1 | [13 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K10G15L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [7 empty] | 1 | [12 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K10G16L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | 1 | [19 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K10G1L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [5 empty] | 1 | [14 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K10G20L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 | [8 empty] | 1 | [11 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-K10G3L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 |  |  |  | 1 | [16 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K10G8L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K10G9L1 | PanelView 1000, 10 in, Grayscale, Keypad, DC | PanelView 1000 | Keypad | 10 in | Grayscale |  | 1 |  | 1 | [18 empty] | DC | 1 | 0.31 | 423 | 280 | 112 | 90 | 338 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC
PanelView | 2711-T10C1 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T10C10 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T10C12 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [20 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T10C14 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color | [8 empty] | 1 | [13 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T10C15 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T10C16 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 | 1 | [19 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T10C20 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T10C3 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 |  |  |  | 1 | [16 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T10C8 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T10C9 | PanelView 1000, 10 in, Color, Touch, AC | PanelView 1000 | Touch | 10 in | Color |  | 1 |  | 1 | [18 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T10C10L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T10C12L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [20 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T10C14L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color | [8 empty] | 1 | [13 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T10C15L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T10C16L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 | 1 | [19 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T10C1L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T10C20L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T10C3L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 |  |  |  | 1 | [16 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T10C8L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T10C9L1 | PanelView 1000, 10 in, Color, Touch, DC | PanelView 1000 | Touch | 10 in | Color |  | 1 |  | 1 | [18 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T10G1 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [5 empty] | 1 | [14 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T10G10 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [6 empty] | 1 | [13 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T10G12 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [20 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T10G14 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale | [8 empty] | 1 | [13 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T10G15 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [7 empty] | 1 | [12 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T10G16 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | 1 | [19 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T10G20 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [8 empty] | 1 | [11 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T10G3 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 |  |  |  | 1 | [16 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T10G8 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T10G9 | PanelView 1000, 10 in, Grayscale, Touch, AC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 |  | 1 | [18 empty] | AC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView | 2711-T10G10L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [6 empty] | 1 | [13 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T10G12L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [20 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T10G14L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale | [8 empty] | 1 | [13 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T10G15L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [7 empty] | 1 | [12 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T10G16L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | 1 | [19 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T10G1L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [5 empty] | 1 | [14 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T10G20L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 | [8 empty] | 1 | [11 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-T10G3L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 |  |  |  | 1 | [16 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T10G8L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 |  |  |  |  | 1 | [15 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T10G9L1 | PanelView 1000, 10 in, Grayscale, Touch, DC | PanelView 1000 | Touch | 10 in | Grayscale |  | 1 |  | 1 | [18 empty] | DC | 1 | 0.31 | 370 | 282 | 112 | 90 | 390 | 257 | Terminals with DH-485 communication require that you upload or download applications by using the communication port. The RS-232 port on these terminals is for printing only. | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Panel cutout is smaller, filler plate required.
PanelView | 2711-K14C1 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-K14C10 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K14C12 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 | [20 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required.
PanelView | 2711-K14C14 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color | [8 empty] | 1 | [13 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-K14C15 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-K14C16 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 | 1 | [19 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required.
PanelView | 2711-K14C20 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required.
PanelView | 2711-K14C3 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 |  |  |  | 1 | [16 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-K14C8 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-K14C9 | PanelView 1400, 14 in, Color, Keypad, AC | PanelView 1400 | Keypad | 14 in | Color |  | 1 |  | 1 | [18 empty] | AC | 1 |  | 483 | 355 | 394 | 370 | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required.
PanelView | 2711-T14C1 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 | [5 empty] | 1 | [14 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView | 2711-T14C10 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 | [6 empty] | 1 | [13 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T14C12 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 | [20 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-T14C14 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color | [8 empty] | 1 | [13 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView | 2711-T14C15 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView | 2711-T14C16 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 | 1 | [19 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-T14C20 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 | [8 empty] | 1 | [11 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required.
PanelView | 2711-T14C3 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 |  |  |  | 1 | [16 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView | 2711-T14C8 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 |  |  |  |  | 1 | [15 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView | 2711-T14C9 | PanelView 1400, 14 in, Color, Touch, AC | PanelView 1400 | Touch | 14 in | Color |  | 1 |  | 1 | [18 empty] | AC | 1 |  | 441 | 355 | 394 | 370 | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required.
PanelView Component | 2711C-F2M | PanelView Component C200, 2 in, Monochrome, Keypad, DC | PanelView Component C200 | Keypad | 2 in | Monochrome |  | s | s | s | [9 empty] | s | [7 empty] | 1 | DC |  |  | 116 | 80 | 54 |  |  |  | Function keys only | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC
PanelView Component | 2711C-K2M | PanelView Component C200, 2 in, Monochrome, Keypad, DC | PanelView Component C200 | Keypad | 2 in | Monochrome |  | s | s | s | [9 empty] | s | [7 empty] | 1 | DC |  |  | 139 | 119 | 55 |  |  |  | Numeric and function keys | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC
PanelView Component | 2711C-T3M | PanelView Component C300, 3 in, Monochrome, Touch, DC | PanelView Component C300 | Touch | 3 in | Monochrome |  | s | s | s | [9 empty] | s | [7 empty] | 1 | DC |  |  | 116 | 80 | 57 |  |  |  |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC
PanelView Component | 2711C-K3M | PanelView Component C300, 3 in, Monochrome, Keypad, DC | PanelView Component C300 | Keypad | 3 in | Monochrome |  | s | s | s | [9 empty] | s | [7 empty] | 1 | DC |  |  | 139 | 119 | 55 |  |  |  |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC
PanelView Component | 2711C-T4T | PanelView Component C400, 4 in, Color, Key/Touch, DC | PanelView Component C400 | Key/Touch | 4 in | Color |  | s | s | s | [6 empty] | 1 |  |  | s | [7 empty] | 1 | DC |  |  | 138 | 113 | 43 |  |  |  |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad.
PanelView Component | 2711C-T6M | PanelView Component C600, 6 in, Monochrome, Touch, DC | PanelView Component C600 | Touch | 6 in | Monochrome |  | s | s | s | [6 empty] | 1 |  |  | s | [7 empty] | 1 | DC |  |  | 209 | 154 | 57 |  |  |  |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView Component | 2711C-T6C | PanelView Component C600, 6 in, Color, Touch, DC | PanelView Component C600 | Touch | 6 in | Color |  | s | s | s | [6 empty] | 1 |  |  | s | [7 empty] | 1 | DC |  |  | 209 | 154 | 57 |  |  |  |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView Component | 2711C-T6T | PanelView Component C600, 6 in, Color, Touch, DC | PanelView Component C600 | Touch | 6 in | Color |  | s | s | s | [6 empty] | 1 |  |  | s | [7 empty] | 1 | DC |  |  | 209 | 154 | 57 |  |  |  |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView Component | 2711C-T10C | PanelView Component C1000, 10 in, Color, Touch, DC | PanelView Component C1000 | Touch | 10 in | Color |  | s | s | s | [6 empty] | 1 |  |  | s | [7 empty] | 1 | DC |  |  | 308 | 250 | 54 |  |  |  |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC
PanelView Enhanced | 2711E-K10C15 | PanelView 1000e, 10.4 in, Color, Keypad, AC | PanelView 1000e | Keypad | 10.4 in | Color | [9 empty] | 1 | [12 empty] | AC |  |  | 423 | 282 | 173 | 156 | 390 | 257 | ControlNet-enhanced release 1.5 2711E-K10C6 terminal | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Enhanced | 2711E-K10C6 | PanelView 1000e, 10.4 in, Color, Keypad, AC | PanelView 1000e | Keypad | 10.4 in | Color |  | 1 |  |  |  |  | s | s | [14 empty] | AC |  |  | 423 | 282 | 173 | 156 | 390 | 257 | clip mount, NEMA 4X | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+ or RIO.
PanelView Enhanced | 2711E-K10C7 | PanelView 1000e, 10.4 in, Color, Keypad, AC | PanelView 1000e | Keypad | 10.4 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC |  |  | 423 | 282 | 173 | 156 | 390 | 257 | ControlNet-enhanced release 1.25 2711E-K10C6 terminal | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Enhanced | 2711E-K12C6 | PanelView 1200e, 12 in, Color, Keypad, AC | PanelView 1200e | Keypad | 12 in | Color |  | 1 |  |  |  |  | s | s | [14 empty] | AC |  |  | 483 | 355 | 383 | 377 | 429 | 326 | stud mount, NEMA 4X (Indoor use only) | 6AV2124-1QC02-0AX0 | KP1500 Comfort, 15.4 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+ or RIO.
PanelView Enhanced | 2711E-K12C6L2 | PanelView 1200e, 12 in, Color, Keypad, AC, Stainless | PanelView 1200e | Keypad | 12 in | Color | Stainless | 1 |  |  |  |  | s | s | [14 empty] | AC |  |  | 483 | 355 | 383 | 377 | 429 | 326 | stud mount, NEMA 4X (Indoor use only) | 6AV2124-1QC02-0AX0 | KP1500 Comfort, 15.4 in, Color, Keypad, DC | Stainless faceplate not available, replacement component IP65. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+ or RIO.
PanelView Enhanced | 2711E-K14C15 | PanelView 1400e, 12 in, Color, Keypad, AC | PanelView 1400e | Keypad | 12 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC |  |  | 483 | 355 | 425 | 404 | 429 | 326 | ControlNet-enhanced release 1.5 2711E-K14C6 terminal | 6AV2124-1QC02-0AX0 | KP1500 Comfort, 15.4 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Enhanced | 2711E-K14C6 | PanelView 1400e, 14 in, Color, Keypad, AC | PanelView 1400e | Keypad | 14 in | Color |  | 1 |  |  |  |  | s | s | [14 empty] | AC |  |  | 483 | 355 | 425 | 404 | 429 | 326 | stud mount, NEMA 4X (Indoor use only) | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+ or RIO.
PanelView Enhanced | 2711E-K14C7 | PanelView 1400e, 14 in, Color, Keypad, AC | PanelView 1400e | Keypad | 14 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC |  |  | 483 | 355 | 425 | 404 | 429 | 326 | ControlNet-enhanced release 1.25 2711E-K14C6 terminal | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Enhanced | 2711E-T10C15 | PanelView 1000e, 10.4 in, Color, Touch, AC | PanelView 1000e | Touch | 10.4 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC |  |  | 370 | 282 | 174 | 157 | 338 | 257 | ControlNet-enhanced release 1.5 2711E-T10C6 terminal | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Enhanced | 2711E-T10C6 | PanelView 1000e, 10.4 in, Color, Touch, AC | PanelView 1000e | Touch | 10.4 in | Color |  | 1 |  |  |  |  | s | s | [14 empty] | AC |  |  | 370 | 282 | 174 | 157 | 338 | 257 | clip mount, NEMA 4X | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+ or RIO.
PanelView Enhanced | 2711E-T10C7 | PanelView 1000e, 10.4 in, Color, Touch, AC | PanelView 1000e | Touch | 10.4 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC |  |  | 370 | 282 | 174 | 157 | 338 | 257 | ControlNet-enhanced release 1.25 2711E-T10C6 terminal | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Enhanced | 2711E-T12C4 | PanelView 1200e, 12 in, Color, Touch, AC | PanelView 1200e | Touch | 12 in | Color |  | 1 | [20 empty] | AC |  |  | 351 | 342 | 389 | 377 | 318 | 316 | stud mount, NEMA 4X (Indoor use only) | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView Enhanced | 2711E-T12C6 | PanelView 1200e, 12 in, Color, Touch, AC | PanelView 1200e | Touch | 12 in | Color |  | 1 |  |  |  |  | s | s | [14 empty] | AC |  |  | 351 | 342 | 389 | 377 | 318 | 318 | clip mount, NEMA 12 | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+ or RIO.
PanelView Enhanced | 2711E-T14C15 | PanelView 1400e, 14 in, Color, Touch, AC | PanelView 1400e | Touch | 14 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC |  |  | 442 | 355 | 423 | 404 | 391 | 326 | ControlNet-enhanced release 1.5 2711E-T14C6 terminal | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Enhanced | 2711E-T14C6 | PanelView 1400e, 14 in, Color, Touch, AC | PanelView 1400e | Touch | 14 in | Color |  | 1 |  |  |  |  | s | s | [14 empty] | AC |  |  | 442 | 355 | 423 | 404 | 391 | 326 | stud mount, NEMA 4X (Indoor use only) | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+ or RIO.
PanelView Enhanced | 2711E-T14C7 | PanelView 1400e, 14 in, Color, Touch, AC | PanelView 1400e | Touch | 14 in | Color |  | 1 | [7 empty] | 1 | [12 empty] | AC |  |  | 442 | 355 | 423 | 404 | 391 | 326 | ControlNet-enhanced release 1.25 2711E-T14C6 terminal | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Plus | 2711P-B4C1A | PanelView Plus 400, 3.5 in, Color, Key/Touch, AC | PanelView Plus 400 | Key/Touch | 3.5 in | Color | [7 empty] | 1 | [13 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B4C20A | PanelView Plus 400, 3.5 in, Color, Key/Touch, AC | PanelView Plus 400 | Key/Touch | 3.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-B4C3A | PanelView Plus 400, 3.5 in, Color, Key/Touch, AC | PanelView Plus 400 | Key/Touch | 3.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-B4C5A | PanelView Plus 400, 3.5 in, Color, Key/Touch, AC | PanelView Plus 400 | Key/Touch | 3.5 in | Color |  | 1 | [19 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-B4C8A | PanelView Plus 400, 3.5 in, Color, Key/Touch, AC | PanelView Plus 400 | Key/Touch | 3.5 in | Color | [6 empty] | 1 | [14 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-B4C10D | PanelView Plus 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.5 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B4C15D | PanelView Plus 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.5 in | Color | [9 empty] | 1 | [11 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Plus | 2711P-B4C1A | PanelView Plus 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.5 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B4C20D | PanelView Plus 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-B4C22D | PanelView Plus 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.5 in | Color |  | 1 | [19 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-B4C3D | PanelView Plus 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-B4C5D | PanelView Plus 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.5 in | Color |  | 1 | [19 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-B4C8D | PanelView Plus 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.5 in | Color | [6 empty] | 1 | [14 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-B4M1A | PanelView Plus 400, 3.7 in, Monochrome, Key/Touch, AC | PanelView Plus 400 | Key/Touch | 3.7 in | Monochrome | [7 empty] | 1 | [13 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B4M8A | PanelView Plus 400, 3.7 in, Monochrome, Key/Touch, AC | PanelView Plus 400 | Key/Touch | 3.7 in | Monochrome | [6 empty] | 1 | [14 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-B4M1D | PanelView Plus 400, 3.7 in, Monochrome, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.7 in | Monochrome | [7 empty] | 1 | [13 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B4M8D | PanelView Plus 400, 3.7 in, Monochrome, Key/Touch, DC | PanelView Plus 400 | Key/Touch | 3.7 in | Monochrome | [6 empty] | 1 | [14 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-K4C1A | PanelView Plus 400, 3.5 in, Color, Keypad, AC | PanelView Plus 400 | Keypad | 3.5 in | Color | [7 empty] | 1 | [13 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-K4C20A | PanelView Plus 400, 3.5 in, Color, Keypad, AC | PanelView Plus 400 | Keypad | 3.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-K4C3A | PanelView Plus 400, 3.5 in, Color, Keypad, AC | PanelView Plus 400 | Keypad | 3.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-K4C5A | PanelView Plus 400, 3.5 in, Color, Keypad, AC | PanelView Plus 400 | Keypad | 3.5 in | Color |  | 1 | [19 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-K4C8A | PanelView Plus 400, 3.5 in, Color, Keypad, AC | PanelView Plus 400 | Keypad | 3.5 in | Color | [6 empty] | 1 | [14 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-K4C1D | PanelView Plus 400, 3.5 in, Color, Keypad, DC | PanelView Plus 400 | Keypad | 3.5 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-K4C20D | PanelView Plus 400, 3.5 in, Color, Keypad, DC | PanelView Plus 400 | Keypad | 3.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-K4C3D | PanelView Plus 400, 3.5 in, Color, Keypad, DC | PanelView Plus 400 | Keypad | 3.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-K4C5D | PanelView Plus 400, 3.5 in, Color, Keypad, DC | PanelView Plus 400 | Keypad | 3.5 in | Color |  | 1 | [19 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-K4C8D | PanelView Plus 400, 3.5 in, Color, Keypad, DC | PanelView Plus 400 | Keypad | 3.5 in | Color | [6 empty] | 1 | [14 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-K4M1A | PanelView Plus 400, 3.7 in, Monochrome, Keypad, AC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome | [7 empty] | 1 | [13 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-K4M20A | PanelView Plus 400, 3.7 in, Monochrome, Keypad, AC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-K4M3A | PanelView Plus 400, 3.7 in, Monochrome, Keypad, AC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-K4M5A | PanelView Plus 400, 3.7 in, Monochrome, Keypad, AC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome |  | 1 | [19 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView Plus | 2711P-K4M8A | PanelView Plus 400, 3.7 in, Monochrome, Keypad, AC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome | [6 empty] | 1 | [14 empty] | 1 | AC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-K4M1D | PanelView Plus 400, 3.7 in, Monochrome, Keypad, DC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome | [7 empty] | 1 | [13 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-K4M20D | PanelView Plus 400, 3.7 in, Monochrome, Keypad, DC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-K4M3D | PanelView Plus 400, 3.7 in, Monochrome, Keypad, DC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-K4M5D | PanelView Plus 400, 3.7 in, Monochrome, Keypad, DC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome |  | 1 | [19 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView Plus | 2711P-K4M8D | PanelView Plus 400, 3.7 in, Monochrome, Keypad, DC | PanelView Plus 400 | Keypad | 3.7 in | Monochrome | [6 empty] | 1 | [14 empty] | 1 | DC |  |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-B6C1A | PanelView Plus 600, 5.5 in, Color, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B6C20A | PanelView Plus 600, 5.5 in, Color, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-B6C3A | PanelView Plus 600, 5.5 in, Color, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-B6C5A | PanelView Plus 600, 5.5 in, Color, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 | [19 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-B6C8A | PanelView Plus 600, 5.5 in, Color, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-B6C10D | PanelView Plus 600, 5.5 in, Color, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B6C15D | PanelView Plus 600, 5.5 in, Color, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Color | [9 empty] | 1 | [11 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Plus | 2711P-B6C1D | PanelView Plus 600, 5.5 in, Color, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B6C20D | PanelView Plus 600, 5.5 in, Color, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-B6C22D | PanelView Plus 600, 5.5 in, Color, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 | [19 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-B6C3D | PanelView Plus 600, 5.5 in, Color, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-B6C5D | PanelView Plus 600, 5.5 in, Color, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 | [19 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-B6C8D | PanelView Plus 600, 5.5 in, Color, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Color |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-B6M1A | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B6M20A | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-B6M3A | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-B6M5A | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 | [19 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-B6M8A | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, AC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-B6M1D | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B6M20D | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-B6M3D | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-B6M5D | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 | [19 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711P-B6M8D | PanelView Plus 600, 5.5 in, Monochrome, Key/Touch, DC | PanelView Plus 600 | Key/Touch | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-K6C1A | PanelView Plus 600, 5.5 in, Color, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-K6C20A | PanelView Plus 600, 5.5 in, Color, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-K6C3A | PanelView Plus 600, 5.5 in, Color, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-K6C5A | PanelView Plus 600, 5.5 in, Color, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 | [19 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView Plus | 2711P-K6C8A | PanelView Plus 600, 5.5 in, Color, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-K6C1D | PanelView Plus 600, 5.5 in, Color, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-K6C20D | PanelView Plus 600, 5.5 in, Color, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-K6C3D | PanelView Plus 600, 5.5 in, Color, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-K6C5D | PanelView Plus 600, 5.5 in, Color, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 | [19 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView Plus | 2711P-K6C8D | PanelView Plus 600, 5.5 in, Color, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Color |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-K6M1A | PanelView Plus 600, 5.5 in, Monochrome, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-K6M20A | PanelView Plus 600, 5.5 in, Monochrome, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-K6M3A | PanelView Plus 600, 5.5 in, Monochrome, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-K6M5A | PanelView Plus 600, 5.5 in, Monochrome, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 | [19 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required.
PanelView Plus | 2711P-K6M8A | PanelView Plus 600, 5.5 in, Monochrome, Keypad, AC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-K6M1D | PanelView Plus 600, 5.5 in, Monochrome, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-K6M20D | PanelView Plus 600, 5.5 in, Monochrome, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-K6M3D | PanelView Plus 600, 5.5 in, Monochrome, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-K6M5D | PanelView Plus 600, 5.5 in, Monochrome, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 | [19 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC
PanelView Plus | 2711P-K6M8D | PanelView Plus 600, 5.5 in, Monochrome, Keypad, DC | PanelView Plus 600 | Keypad | 5.5 in | Monochrome |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 266 | 167 | 98 |  | 241 | 141 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-T6C1A | PanelView Plus 600, 5.5 in, Color, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T6C20A | PanelView Plus 600, 5.5 in, Color, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-T6C3A | PanelView Plus 600, 5.5 in, Color, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-T6C5A | PanelView Plus 600, 5.5 in, Color, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 | [19 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required.
PanelView Plus | 2711P-T6C8A | PanelView Plus 600, 5.5 in, Color, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-T6C10D | PanelView Plus 600, 5.5 in, Color, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T6C15D | PanelView Plus 600, 5.5 in, Color, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Color | [9 empty] | 1 | [11 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses ControlNet.
PanelView Plus | 2711P-T6C1D | PanelView Plus 600, 5.5 in, Color, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T6C20D | PanelView Plus 600, 5.5 in, Color, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-T6C22D | PanelView Plus 600, 5.5 in, Color, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 | [19 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView Plus | 2711P-T6C3D | PanelView Plus 600, 5.5 in, Color, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-T6C5D | PanelView Plus 600, 5.5 in, Color, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 | [19 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView Plus | 2711P-T6C8D | PanelView Plus 600, 5.5 in, Color, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Color |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-T6M1A | PanelView Plus 600, 5.5 in, Monochrome, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T6M20A | PanelView Plus 600, 5.5 in, Monochrome, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Monochrome |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-T6M3A | PanelView Plus 600, 5.5 in, Monochrome, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Monochrome |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-T6M5A | PanelView Plus 600, 5.5 in, Monochrome, Touch, AC | PanelView Plus 600 | Touch | 5.5 in | Monochrome |  | 1 | [19 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required.
PanelView Plus | 2711P-T6M8A | PanelView Plus 600, 5.7 in, Monochrome, Touch, AC | PanelView Plus 600 | Touch | 5.7 in | Monochrome |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | AC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-T6M1D | PanelView Plus 600, 5.5 in, Monochrome, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Monochrome |  | 1 | [5 empty] | 1 |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T6M20D | PanelView Plus 600, 5.5 in, Monochrome, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Monochrome |  | 1 |  |  |  | o | o | o | o | o | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+, RIO, DeviceNet or ControlNet.
PanelView Plus | 2711P-T6M3D | PanelView Plus 600, 5.5 in, Monochrome, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Monochrome |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485.
PanelView Plus | 2711P-T6M5D | PanelView Plus 600, 5.5 in, Monochrome, Touch, DC | PanelView Plus 600 | Touch | 5.5 in | Monochrome |  | 1 | [19 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC
PanelView Plus | 2711P-T6M8D | PanelView Plus 600, 5.7 in, Monochrome, Touch, DC | PanelView Plus 600 | Touch | 5.7 in | Monochrome |  | 1 |  |  |  |  | 1 |  |  |  | 1 | [10 empty] | 1 | DC |  |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH+.
PanelView Plus | 2711P-B7C10D2 | PanelView Plus 700, 6.5 in, Color, Key/Touch, DC | PanelView Plus 700 | Key/Touch | 6.5 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B7C1D2 | PanelView Plus 700, 6.5 in, Color, Key/Touch, DC | PanelView Plus 700 | Key/Touch | 6.5 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T7C10D2 | PanelView Plus 700, 6.5 in, Color, Touch, DC | PanelView Plus 700 | Touch | 6.5 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 246 | 179 | 55 |  | 220 | 154 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T7C1D2 | PanelView Plus 700, 6.5 in, Color, Touch, DC | PanelView Plus 700 | Touch | 6.5 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 246 | 179 | 55 |  | 220 | 154 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B10C10D2 | PanelView Plus 1000, 10.4 in, Color, Key/Touch, DC | PanelView Plus 1000 | Key/Touch | 10.4 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B10C1D2 | PanelView Plus 1000, 10.4 in, Color, Key/Touch, DC | PanelView Plus 1000 | Key/Touch | 10.4 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T10C10D2 | PanelView Plus 1000, 10.4 in, Color, Touch, DC | PanelView Plus 1000 | Touch | 10.4 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T10C1D2 | PanelView Plus 1000, 10.4 in, Color, Touch, DC | PanelView Plus 1000 | Touch | 10.4 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B12C10D2 | PanelView Plus 1250, 12.1 in, Color, Key/Touch, DC | PanelView Plus 1250 | Key/Touch | 12.1 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B12C1D2 | PanelView Plus 1250, 12.1 in, Color, Key/Touch, DC | PanelView Plus 1250 | Key/Touch | 12.1 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T12C10D2 | PanelView Plus 1250, 12.1 in, Color, Touch, DC | PanelView Plus 1250 | Touch | 12.1 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 363 | 282 | 55 |  | 338 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T12C1D2 | PanelView Plus 1250, 12.1 in, Color, Touch, DC | PanelView Plus 1250 | Touch | 12.1 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 363 | 282 | 55 |  | 338 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B15C10D2 | PanelView Plus 1500, 15 in, Color, Key/Touch, DC | PanelView Plus 1500 | Key/Touch | 15 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B15C1D2 | PanelView Plus 1500, 15 in, Color, Key/Touch, DC | PanelView Plus 1500 | Key/Touch | 15 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T15C10D2 | PanelView Plus 1500, 15 in, Color, Touch, DC | PanelView Plus 1500 | Touch | 15 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 416 | 330 | 65 |  | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T15C1D2 | PanelView Plus 1500, 15 in, Color, Touch, DC | PanelView Plus 1500 | Touch | 15 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 416 | 330 | 65 |  | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B7C10D6 | PanelView Plus CE 700, 6.5 in, Color, Key/Touch, DC | PanelView Plus CE 700 | Key/Touch | 6.5 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B7C1D6 | PanelView Plus CE 700, 6.5 in, Color, Key/Touch, DC | PanelView Plus CE 700 | Key/Touch | 6.5 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T7C10D6 | PanelView Plus CE 700, 6.5 in, Color, Touch, DC | PanelView Plus CE 700 | Touch | 6.5 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 246 | 179 | 55 |  | 220 | 154 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T7C1D6 | PanelView Plus CE 700, 6.5 in, Color, Touch, DC | PanelView Plus CE 700 | Touch | 6.5 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 246 | 179 | 55 |  | 220 | 154 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B10C10D6 | PanelView Plus CE 1000, 10.4 in, Color, Key/Touch, DC | PanelView Plus CE 1000 | Key/Touch | 10.4 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B10C1D6 | PanelView Plus CE 1000, 10.4 in, Color, Key/Touch, DC | PanelView Plus CE 1000 | Key/Touch | 10.4 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T10C10D6 | PanelView Plus CE 1000, 10.4 in, Color, Touch, DC | PanelView Plus CE 1000 | Touch | 10.4 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T10C1D6 | PanelView Plus CE 1000, 10.4 in, Color, Touch, DC | PanelView Plus CE 1000 | Touch | 10.4 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B12C10D6 | PanelView Plus CE 1250, 12.1 in, Color, Key/Touch, DC | PanelView Plus CE 1250 | Key/Touch | 12.1 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B12C1D6 | PanelView Plus CE 1250, 12.1 in, Color, Key/Touch, DC | PanelView Plus CE 1250 | Key/Touch | 12.1 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T12C10D6 | PanelView Plus CE 1250, 12.1 in, Color, Touch, DC | PanelView Plus CE 1250 | Touch | 12.1 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 363 | 282 | 55 |  | 338 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T12C1D6 | PanelView Plus CE 1250, 12.1 in, Color, Touch, DC | PanelView Plus CE 1250 | Touch | 12.1 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 363 | 282 | 55 |  | 338 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-B15C10D6 | PanelView Plus CE 1500, 15 in, Color, Key/Touch, DC | PanelView Plus CE 1500 | Key/Touch | 15 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-B15C1D6 | PanelView Plus CE 1500, 15 in, Color, Key/Touch, DC | PanelView Plus CE 1500 | Key/Touch | 15 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711P-T15C10D6 | PanelView Plus CE 1500, 15 in, Color, Touch, DC | PanelView Plus CE 1500 | Touch | 15 in | Color | [8 empty] | 1 | [12 empty] | 1 | DC | 128 |  | 416 | 330 | 65 |  | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DeviceNet.
PanelView Plus | 2711P-T15C1D6 | PanelView Plus CE 1500, 15 in, Color, Touch, DC | PanelView Plus CE 1500 | Touch | 15 in | Color | [7 empty] | 1 | [13 empty] | 1 | DC | 128 |  | 416 | 330 | 65 |  | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses RIO.
PanelView Plus | 2711PC-B4C20D | PanelView Plus Compact 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus Compact 400 | Key/Touch | 3.5 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 20 |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711PC-B4C20D8 | PanelView Plus Compact 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus Compact 400 | Key/Touch | 3.5 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 20 |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711PC-K4M20D | PanelView Plus Compact 400, 3.8 in, Grayscale, Keypad, DC | PanelView Plus Compact 400 | Keypad | 3.8 in | Grayscale |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 20 |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus | 2711PC-K4M20D8 | PanelView Plus Compact 400, 3.5 in, Grayscale, Keypad, DC | PanelView Plus Compact 400 | Keypad | 3.5 in | Grayscale |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 20 |  | 185 | 152 | 90 |  | 156 | 123 |  | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus | 2711PC-T6C20D | PanelView Plus Compact 600, 5.5 in, Color, Touch, DC | PanelView Plus Compact 600 | Touch | 5.5 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 20 |  | 185 | 152 | 98 |  | 156 | 123 | Color TFT Display | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus | 2711PC-T6C20D8 | PanelView Plus Compact 600, 5.7 in, Color, Touch, DC | PanelView Plus Compact 600 | Touch | 5.7 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 20 |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus | 2711PC-T6M20D | PanelView Plus Compact 600, 5.5 in, Color, Touch, DC | PanelView Plus Compact 600 | Touch | 5.5 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 20 |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus | 2711PC-T6M20D8 | PanelView Plus Compact 600, 5.7 in, Color, Touch, DC | PanelView Plus Compact 600 | Touch | 5.7 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 20 |  | 185 | 152 | 98 |  | 156 | 123 |  | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus | 2711PC-T10C4D1 | PanelView Plus Compact 1000, 10.4 in, Color, Touch, DC | PanelView Plus Compact 1000 | Touch | 10.4 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 2 | DC | 25 |  | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B4C20A8 | PanelView Plus 6 400, 3.5 in, Color, Key/Touch, AC | PanelView Plus 6 400 | Key/Touch | 3.5 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B4C5A8 | PanelView Plus 6 400, 3.5 in, Color, Key/Touch, AC | PanelView Plus 6 400 | Key/Touch | 3.5 in | Color |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B4C20D8 | PanelView Plus 6 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 6 400 | Key/Touch | 3.5 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B4C5D8 | PanelView Plus 6 400, 3.5 in, Color, Key/Touch, DC | PanelView Plus 6 400 | Key/Touch | 3.5 in | Color |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K4C20A8 | PanelView Plus 6 400, 3.5 in, Color, Keypad, AC | PanelView Plus 6 400 | Keypad | 3.5 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K4C5A8 | PanelView Plus 6 400, 3.5 in, Color, Keypad, AC | PanelView Plus 6 400 | Keypad | 3.5 in | Color |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K4C20D8 | PanelView Plus 6 400, 3.5 in, Color, Keypad, DC | PanelView Plus 6 400 | Keypad | 3.5 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K4C5D8 | PanelView Plus 6 400, 3.5 in, Color, Keypad, DC | PanelView Plus 6 400 | Keypad | 3.5 in | Color |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K4M20A8 | PanelView Plus 6 400, 3.5 in, Grayscale, Keypad, AC | PanelView Plus 6 400 | Keypad | 3.5 in | Grayscale |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K4M5A8 | PanelView Plus 6 400, 3.5 in, Grayscale, Keypad, AC | PanelView Plus 6 400 | Keypad | 3.5 in | Grayscale |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K4M20D8 | PanelView Plus 6 400, 3.5 in, Grayscale, Keypad, DC | PanelView Plus 6 400 | Keypad | 3.5 in | Grayscale |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K4M5D8 | PanelView Plus 6 400, 3.5 in, Grayscale, Keypad, DC | PanelView Plus 6 400 | Keypad | 3.5 in | Grayscale |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6C20A8 | PanelView Plus 6 600, 5.7 in, Color, Key/Touch, AC | PanelView Plus 6 600 | Key/Touch | 5.7 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6C5A8 | PanelView Plus 6 600, 5.7 in, Color, Key/Touch, AC | PanelView Plus 6 600 | Key/Touch | 5.7 in | Color |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6C20D8 | PanelView Plus 6 600, 5.7 in, Color, Key/Touch, DC | PanelView Plus 6 600 | Key/Touch | 5.7 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6C5D8 | PanelView Plus 6 600, 5.7 in, Color, Key/Touch, DC | PanelView Plus 6 600 | Key/Touch | 5.7 in | Color |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6M20A8 | PanelView Plus 6 600, 5.7 in, Grayscale, Key/Touch, AC | PanelView Plus 6 600 | Key/Touch | 5.7 in | Grayscale |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6M5A8 | PanelView Plus 6 600, 5.7 in, Grayscale, Key/Touch, AC | PanelView Plus 6 600 | Key/Touch | 5.7 in | Grayscale |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6M20D8 | PanelView Plus 6 600, 5.7 in, Grayscale, Key/Touch, DC | PanelView Plus 6 600 | Key/Touch | 5.7 in | Grayscale |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6M5D8 | PanelView Plus 6 600, 5.7 in, Grayscale, Key/Touch, DC | PanelView Plus 6 600 | Key/Touch | 5.7 in | Grayscale |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K6C20A8 | PanelView Plus 6 600, 5.7 in, Color, Keypad, AC | PanelView Plus 6 600 | Keypad | 5.7 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Port | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6C5A8 | PanelView Plus 6 600, 5.7 in, Color, Keypad, AC | PanelView Plus 6 600 | Keypad | 5.7 in | Color |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Port | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6C20D8 | PanelView Plus 6 600, 5.7 in, Color, Keypad, DC | PanelView Plus 6 600 | Keypad | 5.7 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Port | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6C5D8 | PanelView Plus 6 600, 5.7 in, Color, Keypad, DC | PanelView Plus 6 600 | Keypad | 5.7 in | Color |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Port | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6M20A8 | PanelView Plus 6 600, 5.7 in, Grayscale, Keypad, AC | PanelView Plus 6 600 | Keypad | 5.7 in | Grayscale |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Port | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6M5A8 | PanelView Plus 6 600, 5.7 in, Grayscale, Keypad, AC | PanelView Plus 6 600 | Keypad | 5.7 in | Grayscale |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Port | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6M20D8 | PanelView Plus 6 600, 5.7 in, Grayscale, Keypad, DC | PanelView Plus 6 600 | Keypad | 5.7 in | Grayscale |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Port | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6M5D8 | PanelView Plus 6 600, 5.7 in, Grayscale, Keypad, DC | PanelView Plus 6 600 | Keypad | 5.7 in | Grayscale |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Port | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-T6C20A8 | PanelView Plus 6 600, 5.7 in, Color, Touch, AC | PanelView Plus 6 600 | Touch | 5.7 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6C5A8 | PanelView Plus 6 600, 5.7 in, Color, Touch, AC | PanelView Plus 6 600 | Touch | 5.7 in | Color |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6C20D8 | PanelView Plus 6 600, 5.7 in, Color, Touch, DC | PanelView Plus 6 600 | Touch | 5.7 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6C5208 | PanelView Plus 6 600, 5.7 in, Color, Touch, DC | PanelView Plus 6 600 | Touch | 5.7 in | Color |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6C5D8 | PanelView Plus 6 600, 5.7 in, Color, Touch, DC | PanelView Plus 6 600 | Touch | 5.7 in | Color |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6M20A8 | PanelView Plus 6 600, 5.7 in, Grayscale, Touch, AC | PanelView Plus 6 600 | Touch | 5.7 in | Grayscale |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6M5A8 | PanelView Plus 6 600, 5.7 in, Grayscale, Touch, AC | PanelView Plus 6 600 | Touch | 5.7 in | Grayscale |  | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6M20D8 | PanelView Plus 6 600, 5.7 in, Grayscale, Touch, DC | PanelView Plus 6 600 | Touch | 5.7 in | Grayscale |  | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6M5D8 | PanelView Plus 6 600, 5.7 in, Grayscale, Touch, DC | PanelView Plus 6 600 | Touch | 5.7 in | Grayscale |  | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6C20A9 | PanelView Plus 6 600s, 5.7 in, Color, Key/Touch, AC, with Extended Features | PanelView Plus 6 600s | Key/Touch | 5.7 in | Color | with Extended Features | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Ports | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6C5A9 | PanelView Plus 6 600s, 5.7 in, Color, Key/Touch, AC, with Extended Features | PanelView Plus 6 600s | Key/Touch | 5.7 in | Color | with Extended Features | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Ports | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6C20D9 | PanelView Plus 6 600s, 5.7 in, Color, Key/Touch, DC, with Extended Features | PanelView Plus 6 600s | Key/Touch | 5.7 in | Color | with Extended Features | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Ports | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B6C5D9 | PanelView Plus 6 600s, 5.7 in, Color, Key/Touch, DC, with Extended Features | PanelView Plus 6 600s | Key/Touch | 5.7 in | Color | with Extended Features | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Ports | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-K6C20A9 | PanelView Plus 6 600s, 5.7 in, Color, Keypad, AC, with Extended Features | PanelView Plus 6 600s | Keypad | 5.7 in | Color | with Extended Features | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Ports | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6C5A9 | PanelView Plus 6 600s, 5.7 in, Color, Keypad, AC, with Extended Features | PanelView Plus 6 600s | Keypad | 5.7 in | Color | with Extended Features | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Ports | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6C20D9 | PanelView Plus 6 600s, 5.7 in, Color, Keypad, DC, with Extended Features | PanelView Plus 6 600s | Keypad | 5.7 in | Color | with Extended Features | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Ports | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-K6C5D9 | PanelView Plus 6 600s, 5.7 in, Color, Keypad, DC, with Extended Features | PanelView Plus 6 600s | Keypad | 5.7 in | Color | with Extended Features | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 68 |  | 241 | 142 | USB Ports | 6AV2124-1GC01-0AX0 | KP700 Comfort, 7 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required.
PanelView Plus 6 | 2711P-T6C20A9 | PanelView Plus 6 600s, 5.7 in, Color, Touch, AC, with Extended Features | PanelView Plus 6 600s | Touch | 5.7 in | Color | with Extended Features | s | s | s | [6 empty] | 1 | [10 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Ports | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6C5A9 | PanelView Plus 6 600s, 5.7 in, Color, Touch, AC, with Extended Features | PanelView Plus 6 600s | Touch | 5.7 in | Color | with Extended Features | s | s | s | [17 empty] | 2 | AC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Ports | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6C20D9 | PanelView Plus 6 600s, 5.7 in, Color, Touch, DC, with Extended Features | PanelView Plus 6 600s | Touch | 5.7 in | Color | with Extended Features | s | s | s | [6 empty] | 1 | [10 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Ports | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-T6C5D9 | PanelView Plus 6 600s, 5.7 in, Color, Touch, DC, with Extended Features | PanelView Plus 6 600s | Touch | 5.7 in | Color | with Extended Features | s | s | s | [17 empty] | 2 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Ports | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711P-B7C4A8 | PanelView Plus 6 700, 6.5 in, Color, Key/Touch, AC | PanelView Plus 6 700 | Key/Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B7C4A9 | PanelView Plus 6 700, 6.5 in, Color, Key/Touch, AC | PanelView Plus 6 700 | Key/Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B7C5A8 | PanelView Plus 6 700, 6.5 in, Color, Key/Touch, AC | PanelView Plus 6 700 | Key/Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B7C4D8 | PanelView Plus 6 700, 6.5 in, Color, Key/Touch, DC | PanelView Plus 6 700 | Key/Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 | 2 USB Ports, DH+, DH-485, ControlNet, Ethernet available with add-on module | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B7C4D9 | PanelView Plus 6 700, 6.5 in, Color, Key/Touch, DC | PanelView Plus 6 700 | Key/Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K7C4A8 | PanelView Plus 6 700, 6.5 in, Color, Keypad, AC | PanelView Plus 6 700 | Keypad | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-1JC01-0AX0 | KP900 Comfort, 9 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K7C4A9 | PanelView Plus 6 700, 6.5 in, Color, Keypad, AC | PanelView Plus 6 700 | Keypad | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-1JC01-0AX0 | KP900 Comfort, 9 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K7C4D8 | PanelView Plus 6 700, 6.5 in, Color, Keypad, DC | PanelView Plus 6 700 | Keypad | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 | 2 USB Ports, DH+, DH-485, ControlNet, Ethernet available with add-on module | 6AV2124-1JC01-0AX0 | KP900 Comfort, 9 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K7C4D9 | PanelView Plus 6 700, 6.5 in, Color, Keypad, DC | PanelView Plus 6 700 | Keypad | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 290 | 193 | 55 |  | 264 | 167 |  | 6AV2124-1JC01-0AX0 | KP900 Comfort, 9 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T7C4A8 | PanelView Plus 6 700, 6.5 in, Color, Touch, AC | PanelView Plus 6 700 | Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 246 | 179 | 55 |  | 220 | 154 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T7C4A9 | PanelView Plus 6 700, 6.5 in, Color, Touch, AC | PanelView Plus 6 700 | Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 246 | 179 | 55 |  | 220 | 154 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T7C4D8 | PanelView Plus 6 700, 6.5 in, Color, Touch, DC | PanelView Plus 6 700 | Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 246 | 179 | 55 |  | 220 | 154 | 2 USB Ports, DH+, DH-485, ControlNet, Ethernet available with add-on module | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T7C4D8K | PanelView Plus 6 700, 6.5 in, Color, Touch, DC, Conformal Coated | PanelView Plus 6 700 | Touch | 6.5 in | Color | Conformal Coated | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 246 | 179 | 55 |  | 220 | 154 |  | 6AG1124-0JC01-4AX0 | TP900 Comfort SIPLUS, 9 in, Color, Touch, DC, Conformal Coated | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T7C4D9 | PanelView Plus 6 700, 6.5 in, Color, Touch, DC | PanelView Plus 6 700 | Touch | 6.5 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 246 | 179 | 55 |  | 220 | 154 |  | 6AV2124-0JC01-0AX0 | TP900 Comfort, 9 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B10C4A8 | PanelView Plus 6 1000, 10.4 in, Color, Key/Touch, AC | PanelView Plus 6 1000 | Key/Touch | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B10C4A9 | PanelView Plus 6 1000, 10.4 in, Color, Key/Touch, AC | PanelView Plus 6 1000 | Key/Touch | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B10C4D8 | PanelView Plus 6 1000, 10.4 in, Color, Key/Touch, DC | PanelView Plus 6 1000 | Key/Touch | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B10C4D9 | PanelView Plus 6 1000, 10.4 in, Color, Key/Touch, DC | PanelView Plus 6 1000 | Key/Touch | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K10C4A8 | PanelView Plus 6 1000, 10.4 in, Color, Keypad, AC | PanelView Plus 6 1000 | Keypad | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K10C4A9 | PanelView Plus 6 1000, 10.4 in, Color, Keypad, AC | PanelView Plus 6 1000 | Keypad | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K10C4D8 | PanelView Plus 6 1000, 10.4 in, Color, Keypad, DC | PanelView Plus 6 1000 | Keypad | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K10C4D9 | PanelView Plus 6 1000, 10.4 in, Color, Keypad, DC | PanelView Plus 6 1000 | Keypad | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 399 | 248 | 55 |  | 375 | 224 |  | 6AV2124-1MC01-0AX0 | KP1200 Comfort, 12.1 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T10C4A8 | PanelView Plus 6 1000, 10.4 in, Color, Touch, AC | PanelView Plus 6 1000 | Touch | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T10C4A9 | PanelView Plus 6 1000, 10.4 in, Color, Touch, AC | PanelView Plus 6 1000 | Touch | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T10C4D8 | PanelView Plus 6 1000, 10.4 in, Color, Touch, DC | PanelView Plus 6 1000 | Touch | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T10C4D9 | PanelView Plus 6 1000, 10.4 in, Color, Touch, DC | PanelView Plus 6 1000 | Touch | 10.4 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 329 | 248 | 55 |  | 305 | 224 |  | 6AV2124-0MC01-0AX0 | TP1200 Comfort, 12.1 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B12C4A8 | PanelView Plus 6 1250, 12.1 in, Color, Key/Touch, AC | PanelView Plus 6 1250 | Key/Touch | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B12C4A9 | PanelView Plus 6 1250, 12.1 in, Color, Key/Touch, AC | PanelView Plus 6 1250 | Key/Touch | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B12C4D8 | PanelView Plus 6 1250, 12.1 in, Color, Key/Touch, DC | PanelView Plus 6 1250 | Key/Touch | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B12C4D9 | PanelView Plus 6 1250, 12.1 in, Color, Key/Touch, DC | PanelView Plus 6 1250 | Key/Touch | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K12C4A8 | PanelView Plus 6 1250, 12.1 in, Color, Keypad, AC | PanelView Plus 6 1250 | Keypad | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-1QC02-0AX0 | KP1500 Comfort, 15.4 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K12C4A9 | PanelView Plus 6 1250, 12.1 in, Color, Keypad, AC | PanelView Plus 6 1250 | Keypad | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-1QC02-0AX0 | KP1500 Comfort, 15.4 in, Color, Keypad, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K12C4D8 | PanelView Plus 6 1250, 12.1 in, Color, Keypad, DC | PanelView Plus 6 1250 | Keypad | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-1QC02-0AX0 | KP1500 Comfort, 15.4 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K12C4D9 | PanelView Plus 6 1250, 12.1 in, Color, Keypad, DC | PanelView Plus 6 1250 | Keypad | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 416 | 282 | 55 |  | 390 | 257 |  | 6AV2124-1QC02-0AX0 | KP1500 Comfort, 15.4 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T12C4A8 | PanelView Plus 6 1250, 12.1 in, Color, Touch, AC | PanelView Plus 6 1250 | Touch | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 363 | 282 | 55 |  | 338 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T12C4A9 | PanelView Plus 6 1250, 12.1 in, Color, Touch, AC | PanelView Plus 6 1250 | Touch | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 363 | 282 | 55 |  | 338 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T12C4D8 | PanelView Plus 6 1250, 12.1 in, Color, Touch, DC | PanelView Plus 6 1250 | Touch | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 363 | 282 | 55 |  | 338 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T12C4D8K | PanelView Plus 6 1250, 12.1 in, Color, Touch, DC, Conformal Coated | PanelView Plus 6 1250 | Touch | 12.1 in | Color | Conformal Coated | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 363 | 282 | 55 |  | 338 | 257 |  | 6AG1124-0QC02-4AX0 | TP1500 Comfort SIPLUS, 15.4 in, Color, Touch, DC, Conformal Coated | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T12C4D9 | PanelView Plus 6 1250, 12.1 in, Color, Touch, DC | PanelView Plus 6 1250 | Touch | 12.1 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 363 | 282 | 55 |  | 338 | 257 |  | 6AV2124-0QC02-0AX0 | TP1500 Comfort, 15.4 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B15C4A8 | PanelView Plus 6 1500, 15 in, Color, Key/Touch, AC | PanelView Plus 6 1500 | Key/Touch | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B15C4A9 | PanelView Plus 6 1500, 15 in, Color, Key/Touch, AC | PanelView Plus 6 1500 | Key/Touch | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B15C4D8 | PanelView Plus 6 1500, 15 in, Color, Key/Touch, DC | PanelView Plus 6 1500 | Key/Touch | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-B15C4D9 | PanelView Plus 6 1500, 15 in, Color, Key/Touch, DC | PanelView Plus 6 1500 | Key/Touch | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K15C4A8 | PanelView Plus 6 1500, 15 in, Color, Keypad, AC | PanelView Plus 6 1500 | Keypad | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K15C4A9 | PanelView Plus 6 1500, 15 in, Color, Keypad, AC | PanelView Plus 6 1500 | Keypad | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K15C4D8 | PanelView Plus 6 1500, 15 in, Color, Keypad, DC | PanelView Plus 6 1500 | Keypad | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-K15C4D9 | PanelView Plus 6 1500, 15 in, Color, Keypad, DC | PanelView Plus 6 1500 | Keypad | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 469 | 330 | 65 |  | 419 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Touch panel, no keypad. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T15C4A8 | PanelView Plus 6 1500, 15 in, Color, Touch, AC | PanelView Plus 6 1500 | Touch | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 416 | 330 | 65 |  | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T15C4A9 | PanelView Plus 6 1500, 15 in, Color, Touch, AC | PanelView Plus 6 1500 | Touch | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | AC | 512 | 512 | 416 | 330 | 65 |  | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Conversion from AC to DC. DC power supply required. Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T15C4D8 | PanelView Plus 6 1500, 15 in, Color, Touch, DC | PanelView Plus 6 1500 | Touch | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 416 | 330 | 65 |  | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711P-T15C4D9 | PanelView Plus 6 1500, 15 in, Color, Touch, DC | PanelView Plus 6 1500 | Touch | 15 in | Color |  | s | s | s |  | o | o |  |  | o | 1 | [10 empty] | 3 | DC | 512 | 512 | 416 | 330 | 65 |  | 391 | 305 |  | 6AV2124-0UC02-0AX0 | TP1900 Comfort, 18.5 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Confirm communication bus in use. Bus gateway may be required or bus may need to be converted if application uses DH-485, DH+ or ControlNet.
PanelView Plus 6 | 2711PC-B4C20D8 | PanelView Plus 6 Compact 400s, 3.5 in, Color, Key/Touch, DC | PanelView Plus 6 Compact 400s | Key/Touch | 3.5 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-2DC01-0AX0 | KTP400 Comfort, 4.3 in, Color, Key/Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711PC-K4M20D8 | PanelView Plus 6 Compact 400s, 3.5 in, Grayscale, Keypad, DC | PanelView Plus 6 Compact 400s | Keypad | 3.5 in | Grayscale |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 256 | 512 | 185 | 152 | 90 |  | 156 | 123 | USB Port | 6AV2124-1DC01-0AX0 | KP400 Comfort, 4.3 in, Color, Keypad, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711PC-T6C20D8 | PanelView Plus 6 Compact 600s, 5.7 in, Color, Touch, DC | PanelView Plus 6 Compact 600s | Touch | 5.7 in | Color |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
PanelView Plus 6 | 2711PC-T6M20D8 | PanelView Plus 6 Compact 600s, 5.7 in, Grayscale, Touch, DC | PanelView Plus 6 Compact 600s | Touch | 5.7 in | Grayscale |  | 1 | [8 empty] | 1 | [10 empty] | 1 | DC | 256 | 512 | 266 | 167 | 98 |  | 241 | 142 | USB Port | 6AV2124-0GC01-0AX0 | TP700 Comfort, 7 in, Color, Touch, DC | Confirm project memory requirements. Upgrade of MMC may be required. Panel cutout is smaller, filler plate required.
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 214 | 158 |  |  | 197 | 141
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 274 | 190 |  |  | 251 | 166
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 330 | 241 |  |  | 310 | 221
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 24 |  | 415 | 310 |  |  | 396 | 291
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 24 |  | 483 | 337 |  |  | 465 | 319
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 24 |  | 560 | 380 |  |  | 542 | 362
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 1 | DC | 4 |  | 152 | 188 |  |  | 135 | 171
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 308 | 204 |  |  | 281 | 177
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 362 | 230 |  |  | 338 | 206
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 454 | 289 |  |  | 434 | 269
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 24 |  | 483 | 310 |  |  | 450 | 291
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 1 | DC | 4 |  | 140 | 116 |  |  | 123 | 99
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 214 | 158 |  |  | 197 | 141
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 274 | 190 |  |  | 251 | 166
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 330 | 241 |  |  | 310 | 221
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 24 |  | 415 | 310 |  |  | 396 | 291
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 24 |  | 483 | 337 |  |  | 465 | 319
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 24 |  | 560 | 380 |  |  | 542 | 362
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 1 | DC | 4 |  | 152 | 188 |  |  | 135 | 171
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 308 | 204 |  |  | 281 | 177
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 362 | 230 |  |  | 338 | 206
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 12 |  | 454 | 289 |  |  | 434 | 269
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 2 | DC | 24 |  | 483 | 310 |  |  | 450 | 291
[8 empty] | 1 | 1 |  | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 |  | 1 | DC | 4 |  | 140 | 116 |  |  | 123 | 99